## Start
1 af = 325,851 gallons
1 MG = 3.069 af
| New Water Source Impact Tool |  | Results:
| Start: |  | Energy Consumption:
| 1) What state do you live in? |  | #N/A | Kilowatt hours of electricity per year
|  |  | #N/A | Kilowatt hours of electricity per million gallons of water delivered
| 2) What type of source is the new supply? |  | CO2 Emmissions:
|  |  | #N/A | Lbs. CO2 emissions per year
| 3) How much water (in MG/year) do expect to provide from this source? |  | #N/A | Lbs. CO2 emissions per million gallons of water delivered
Water Consumption (from electricity generation):
| 4) How many feet in elevation will the water be lifted? |  | #N/A | gallons of H2O per year
|  |  | #N/A | gallons of H2O per million gallons of water delivered
| 5) What is the energy intensity (in kWh/MG) of your distribution system? |  | Energy Costs:
If unsure, use 644 kWh/MG as a default value, or 0 if you would not like to factor in local distribution
|  |  | #N/A | Cost of electricity per year*
|  |  | #N/A | Cost of electricity per million gallons of water delivered*
6) What percentage of water is lost due to leaks in your water system?
If unsure, 10% is typical for U.S. water systems
Disclaimer:
River Network’s Water/Energy Calculators are interactive tools designed to help you figure out how much how much energy and carbon emissions are embedded in the water you use. Results received from this calculator are designed for indication purposes only. River Network does not guarantee the accuracy of any information derived from this tool, and is not responsible for any errors, omissions, or misrepresentations. For assumptions, see "Assumptions" tab.
7) What is the average pumping efficiency?
70% is typically the optimal efficiency for a pumping system
*Based on residential retail rates. Water utitlities typically buy electricity at discounted rates, therefore actual electricity costs incured by the utility would likely be lower, however, residential rates are a better reflection of the "avoided costs" that would result if a new water supply is avoided. Avoided cost is the incremental cost to an electric utility for capacity or energy or both that, but for the acquisition of energy or capacity from another source, the utility would have to incur.
Please send any questions or comments to bgriffiths@rivernetwork.org
This tool was designed by Bevan Griffiths Sattenspiel

## Assumptions
Assumptions:
Pumping Factors:
Source Types*: | Energy (kWh/af) | (kWh/MG) |  | Overall pumping efficiency | kWh to lift one MG one foot in elevation***
Surface Water | 0 | 0 |  | 75% | 4.2
Recycled Water | 350 | 1074.15 |  | 70% | 4.48
Brackish Groundwater | 1050 | 3222.45 |  | 65% | 4.85
Groundwater | 650 | 1994.85 |  | 60% | 5.25
Desalinated Seawater | 4500 | 13810.5 |  | 55% | 5.71
|  |  |  | 50% | 6.29
Generic Water Treatment | 55 | 168.795 |  | 45% | 7
Generic Distribution** |  | 644 |  | 40% | 7.86
1 af = 325,851 gallons |  |  |  |  | #N/A
1 MG = 3.069 af | #N/A | #N/A
*From Pacific Institute's Water to Air Model Manual, pg. 28 <http://www.pacinst.org/resources/water_to_air_models/index.htm>
**From Greenhouse Gas and Energy Co-Benefits of Water Conservation, by Carol Maas from the POLIS Water Sustainability Project <http://www.poliswaterproject.org/publication/91>
***From UC Davis <http://cetulare.ucdavis.edu/pubgrape/ig696.htm>
| Avg. Residential Electicity Cost, by Sate (April 2009)* |  |  | Carbon Intensity of Electricity, by State** |  |  | Water Intensity of Electricity, by State***
| State | USD$/kWh |  | State | lbs. CO2/kWh |  | State | gallons H2O/kWh
|  |  | #N/A |  |  | #N/A |  |  | #N/A
| U.S. Average | 0.1103 |  | U.S. Average | 1.36 |  | U.S. Average | 2
| Alabama | 0.1031 |  | Alabama | 1.2987 |  | Alabama | 2.5
| Alaska | 0.1725 |  | Alaska | 1.1065 |  | Alaska | 0.27
| Arizona | 0.0951 |  | Arizona | 1.2189 |  | Arizona | 7.85
| Arkansas | 0.0894 |  | Arkansas | 1.2803 |  | Arkansas | 0.26
| California | 0.1495 |  | California | 0.7004 |  | California | 4.64
| Colorado | 0.0925 |  | Colorado | 1.9861 |  | Colorado | 1.2
| Connecticut | 0.1949 |  | Connecticut | 0.75419 |  | Connecticut | 0.07
| Delaware | 0.1325 |  | Delaware | 1.8037 |  | Delaware | 0.01
| District of Columbia | 0.1283 |  | District of Columbia | 3.6143 |  | District of Columbia | 1.61
| Florida | 0.1243 |  | Florida | 1.348 |  | Florida | 0.14
| Georgia | 0.094 |  | Georgia | 1.3883 |  | Georgia | 1.65
| Hawaii | 0.2576 |  | Hawaii | 1.6547 |  | Hawaii | 0.04
| Idaho | 0.0705 |  | Idaho | 0.14394 |  | Idaho | 7.85
| Illinois | 0.1078 |  | Illinois | 1.1548 |  | Illinois | 1.05
| Indiana | 0.0862 |  | Indiana | 2.098 |  | Indiana | 0.41
| Iowa | 0.0888 |  | Iowa | 1.9433 |  | Iowa | 0.11
| Kansas | 0.0816 |  | Kansas | 1.8706 |  | Kansas | 0.58
| Kentucky | 0.081 |  | Kentucky | 2.0511 |  | Kentucky | 5.32
| Louisiana | 0.0892 |  | Louisiana | 1.2012 |  | Louisiana | 1.47
| Maine | 0.1603 |  | Maine | 0.77183 |  | Maine | 0.12
| Maryland | 0.144 |  | Maryland | 1.293 |  | Maryland | 0.21
| Massachusetts | 0.1812 |  | Massachusetts | 1.2261 |  | Massachusetts | 0
| Michigan | 0.1117 |  | Michigan | 1.4127 |  | Michigan | 0.48
| Minnesota | 0.0959 |  | Minnesota | 1.5875 |  | Minnesota | 0.41
| Mississippi | 0.0964 |  | Mississippi | 1.409 |  | Mississippi | 0.37
| Missouri | 0.0702 |  | Missouri | 1.8814 |  | Missouri | 0.3
| Montana | 0.0844 |  | Montana | 1.5729 |  | Montana | 16.74
| Nebraska | 0.0689 |  | Nebraska | 1.5031 |  | Nebraska | 0.3
| Nevada | 0.1223 |  | Nevada | 1.5727 |  | Nevada | 7.25
| New Hampshire | 0.1629 |  | New Hampshire | 0.77927 |  | New Hampshire | 0.1
| New Jersey | 0.158 |  | New Jersey | 0.71279 |  | New Jersey | 0.07
| New Mexico | 0.0954 |  | New Mexico | 1.992 |  | New Mexico | 1.13
| New York | 0.1746 |  | New York | 0.90716 |  | New York | 1.62
| North Carolina | 0.0945 |  | North Carolina | 1.2178 |  | North Carolina | 0.55
| North Dakota | 0.0655 |  | North Dakota | 2.3863 |  | North Dakota | 5.13
| Ohio | 0.0939 |  | Ohio | 1.779 |  | Ohio | 0.94
| Oklahoma | 0.0767 |  | Oklahoma | 1.726 |  | Oklahoma | 8.39
| Oregon | 0.0841 |  | Oregon | 0.45579 |  | Oregon | 3.71
| Pennsylvania | 0.1083 |  | Pennsylvania | 1.2162 |  | Pennsylvania | 0.53
| Rhode Island | 0.172 |  | Rhode Island | 1.071 |  | Rhode Island | 0
| South Carolina | 0.098 |  | South Carolina | 0.91482 |  | South Carolina | 0.25
| South Dakota | 0.0758 |  | South Dakota | 1.2154 |  | South Dakota | 72.64
| Tennessee | 0.0944 |  | Tennessee | 1.266 |  | Tennessee | 3.6
| Texas | 0.1279 |  | Texas | 1.4716 |  | Texas | 0.43
| Utah | 0.08 |  | Utah | 2.1208 |  | Utah | 3.05
| Vermont | 0.1437 |  | Vermont | 0.006939 |  | Vermont | 0.25
| Virginia | 0.1001 |  | Virginia | 1.2105 |  | Virginia | 0.06
| Washington | 0.0765 |  | Washington | 0.35993 |  | Washington | 2.7
| West Virginia | 0.074 |  | West Virginia | 1.988 |  | West Virginia | 0.58
| Wisconsin | 0.1235 |  | Wisconsin | 1.7129 |  | Wisconsin | 0.46
| Wyoming | 0.0776 |  | Wyoming | 2.2775 |  | Wyoming | 4.15
*Energy Information Administration, Table 5.6.B, January 2009 <http://www.epa.gov/cleanenergy/energy-resources/egrid/index.html>
**U.S. EPA's eGRID 2006 Version 2.1 <http://www.epa.gov/cleanenergy/energy-resources/egrid/index.html>
***Consumptive Water Use for U.S. Power Production.” National Renewable Energy Laboratory, 2003 <http://www.nrel.gov/docs/fy04osti/33905.pdf>